Amador Fire Protection District

Emergency Water Storage Tank Standard

Amador County Ordinance #15.30.360

A water tank is NOT REQUIRED if a hydrant is located

within 1000 ft. of the property.

- 2500 gallons minimum water supply for fire department use only.

- Minimum 50 feet from structures.

- Maximum 12 feet from the fire department access road.

- FD access road weight load shall hold 40,000 lbs. during all weather.

- Brass outlet at least 18-inch off the ground.

- Minimum Pipe Size shall be 4 ½-inch.

- Outlet shall be a brass 4 ½-inch N.H.T male threads.

- Minimum 10 square inch air vent shall be provided.

- Pad shall be a minimum 3-inch aggregate rock base and 24-inches wider than the tank.

- A blue reflective address mounted on the tank visible from the roadway.

- Letterings for the mounted address shall be a minimum 4-inch in height with a minimum stroke width of ½ inch.

- Tanks to be constructed of molded plastic, fiberglass or galvanized steel, not less than 12 gauge.

- A water capacity or site glass indicator is optional.

10 Sq. Inch Air Vent Minimum 3/8” Rust Resistant Screen

Site Glass (Optional)

Home

4” Min Pipe Size

4 ½” Brass (optional) Male Thread

Tanks 50 Ft. Away

2,500 Gallons Minimum Reflective Blue Address

18” Min From Grade

3” Min. Rock Base 2 Ft. Wider Than Tank

12 Ft. Max From FD Access Road

A site inspection is required prior to installation of the tank and finalization of the project. Contact Fire Prevention Officer to schedule appointment: (209) 223-6226.

www.amadorfire.org

810 Court Street, Jackson, CA 95642-2132           Rev: 01-07-26